IntelliRail

Intelli-RFID Reader ⇄ Delta DVP-12SA2

PLC Integration Specification

| Item | Detail |
| --- | --- |
| Document | PLC Integration Specification — Intelli-RFID Reader to Delta DVP-12SA2 |
| Revision | 1.0 |
| Date | 30 August 2026 |
| Reader unit | Intelli-RFID Reader, connector J26 |
| PLC | Delta DVP12SA211R — 12-point, RELAY output variant (see §2) |
| Application | Retail warehouse RFID tunnel — conveyor speed, direction, read result, and controlled shutdown |
| Audience | PLC programmer and control panel builder |
| Prepared by | IntelliRail |

How to read this document Sections 2–4 must be built exactly as written. They are electrical and they have been got wrong before; the failure modes are described so they can be recognised. Section 5.3 defines an encoded signal. The read verdict is carried on one channel by pulse width. The decoding rule is not a detail — decoding it loosely turns a failed read into a passed one. Section 6 is the shutdown sequence. It exists to prevent a specific, silent data corruption. Section 7 is the ladder specification. Each requirement is numbered R1–R14 so it can be signed off individually. Section 8 is a safety statement and must be read before design. This interface is NOT a safety function. Section 11 lists what we still need from you. Six of those answers are needed before the ladder can be finished.

# Contents

| Section | Page |
| --- | --- |
| 1. What you are integrating with | 3 |
| 2. PLC selection | 3 |
| 3. Wiring — panel builder section | 5 |
| 4. I/O map | 7 |
| 5. Signal semantics | 9 |
| 6. Clean shutdown and power-up | 12 |
| 7. Ladder requirements | 15 |
| 8. Safety statement — please read before design | 17 |
| 9. Enclosure and environment | 18 |
| 10. Commissioning checklist | 19 |
| 11. What we still need to confirm | 21 |
| Appendix A. Quick reference | 23 |

# 1. What you are integrating with

The Intelli-RFID Reader reads RFID tags on cartons passing through a conveyor tunnel and reports the result. It exposes eleven electrically isolated field I/O channels on a single 12-way connector (J26), and those channels are the entire interface between the reader and your PLC.

The division of responsibility is fixed and is not a matter of preference:

- The reader decides. It determines what speed the conveyor should run at, in which direction, and whether the carton read succeeded.

- The PLC acts. It receives those signals, applies its own interlocks and logic, and drives the VFD or whatever moves the conveyor.

- The PLC reports back — telling the reader when a carton has arrived in and left the reading zone, and requesting a controlled shutdown.

The reader never talks to the VFD Every reader output lands on a DVP input. Nothing on the reader side ever connects to a variable frequency drive, a contactor, a stack light or a relay coil. This is an architectural constraint, not an observation. The reader's outputs are optocoupler open-collector devices sized for the DVP's 2.94 mA input demand. A VFD input typically draws 5–10 mA and is outside what they can guarantee. If the panel is later "simplified" by taking SPEED or DIRECTION straight to a drive, it will not work — and it will fail intermittently and when hot, rather than cleanly.

Electrically, all eleven channels share a single return, FIELD_COM (J26 pin 8), which is the field supply 0 V. The reader board's own internal ground is isolated from FIELD_COM by a 2500 Vrms optocoupler barrier. Section 3.4 explains why that barrier must not be defeated by earthing.

# 2. PLC selection

## 2.1 Why a relay output variant is mandatory

A sinking (NPN) transistor output physically cannot drive this reader. The reader's inputs (IN1–IN4) require +24 V to be applied to the input pin. The return path is hard-wired internally to FIELD_COM; nothing else energises them. An NPN output can only pull its terminal down to 0 V — it cannot source 24 V. The “…T” variants are therefore ruled out, and there is no PNP transistor variant in the 12-point size. For a DVP-12SA2 the choice is relay or nothing.

| Variant | Points | Output type | Suitable? |
| --- | --- | --- | --- |
| DVP12SA211R | 8 in / 4 out | Relay, dry contact | YES — specified for this project |
| DVP12SA211T | 8 in / 4 out | Transistor, NPN sinking | NO — cannot source 24 V |
| DVP28SA211R / S | 16 in / 12 out | Relay / PNP transistor | Not required. See 2.2 before considering it. |

## 2.2 The 12-point unit fits — but only just, and only by design

Every point on this PLC is allocated. That is a deliberate choice rather than an oversight: two signals were merged specifically to avoid forcing a larger unit for the sake of one channel.

|  | Used | Free |
| --- | --- | --- |
| Inputs (X0–X7) | 7 — six reader signals plus the shutdown button | 1 — X0, reserved for a future encoder |
| Outputs (Y0–Y3) | 4 — three reader signals plus the status lamp | 0 |

Two consequences you should know before building the panel 1. The read verdict shares one channel. Pass and fail are not separate wires. One channel carries both, encoded by pulse width — see §5.3. This is what freed a channel for the heartbeat. 2. One status lamp, not two. Reader-ready and safe-to-power-down are shown on a single lamp by flash pattern — see §6.5. This is what freed an output for the lamp at all. There is no spare capacity left. Any further signal in either direction needs a 28-point unit (DVP28SA211R) or an expansion module. Raise it now rather than after the panel is built.

## 2.3 The relay case checks out

| Check | Figure | Verdict |
| --- | --- | --- |
| Load current the reader presents | ≈ 3.36 mA at 24 V (2.30 mA at 16.8 V, 4.24 mA at 30 V) | — |
| Relay minimum load | 1 mA / 5 V | 3.4× above it — enough wetting current that contact oxide is not a concern |
| Relay maximum load | 1.5 A per point, 4 A per common | 450× under — irrelevant, and ample for the lamp |
| Working voltage | 5–30 VDC | 24 V is comfortably inside |
| Response time | ≈ 10 ms | Acceptable — these are permissive and status signals, and the reader debounces ≥ 10 ms anyway |
| Output common | All four Y outputs share C0 on the 12-point relay model | Matches the reader's single shared FIELD_COM — one wire from C0 to +24 V serves all four, lamp included |

The shared C0 is specific to the 12-point relay model. The 28-point relay model splits its commons, so if the unit is ever changed the output wiring must be revisited.

# 3. Wiring — panel builder section

Pull all twelve cores to the reader. Ten of them land on PLC points; two are parked on spare terminals so that adding them later is a jumper rather than a re-pull.

## 3.1 The complete wiring list

| From | To |
| --- | --- |
| Field supply +24 V | PLC 24V terminal, PLC S/S terminal, and PLC C0 terminal — jumper S/S to C0 |
| Field supply 0 V | PLC 0V terminal, and J26 pin 8 (FIELD_COM) |
| J26 pins 1–6 (OUT1…OUT6) | PLC X1 … X6 |
| J26 pin 7 (OUT7) | Spare terminal — PARKED, not connected to the PLC |
| J26 pins 9–11 (IN1…IN3) | PLC Y0 … Y2 |
| J26 pin 12 (IN4) | Spare terminal — PARKED, not connected to the PLC |
| Shutdown push button | PLC X7 (panel-local, not in the field harness) |
| Status lamp | PLC Y3, lamp wired between Y3 and 0 V (panel-local) |

This is Delta's SINK mode for the inputs (instruction sheet Figure 5). Do not write only “sink mode” on a drawing — write the physical statement. The term is used both ways round in the field, and reversing S/S produces a system in which nothing ever turns on and nothing reports a fault.

Why park OUT7 and IN4 rather than omit them Both are real, wired channels on the reader that this design does not currently use. Pulling them now costs two cores in a harness that is being made anyway; adding them later means re-pulling a field cable, which is not. Land them on numbered spare terminals in the panel and mark them on the drawing. If a future signal is needed, it becomes a jumper — provided a PLC point is free, which today it is not (§2.2).

## 3.2 Three things this table is quietly saying

Each of these has been got wrong before. They are stated as failure modes so they can be recognised on site.

1. C0 is the +24 V side, not a ground. C0 is the dry relay common that lets Y0–Y2 push +24 V into the reader's inputs, and that also feeds the lamp on Y3. Feeding it does NOT establish the reference between board and PLC. The common is the separate FIELD_COM → supply 0 V wire. Without that wire the relay outputs have no return path and nothing works.

2. S/S must go to +24 V as well, or all six reader outputs do nothing. S/S and C0 are internally isolated from one another, so one +24 V wire landing on both terminals is correct and normal — it is not a short.

3. The reader takes no +24 V feed on J26. J26 has no 24 V pin. The reader's outputs are open-collector sinks and its inputs are fed by the PLC's own relay contacts. Only the 0 V return reaches the board on this connector. If you are working from any earlier drawing that shows a separate 2-pin 24 V feed to J26, that belongs to a different (interposer) arrangement and must not be carried over.

## 3.3 The 24 V supply — one supply, and the PLC sets its floor

- A single 24 V supply and a single return serve every device on J26. Split field supplies are not permitted.

- The PLC, not the reader, sets the low-voltage limit. The reader's field I/O works down to 16.8 V. The DVP-SA2 stops below 17.5 V and drops every output. Specify and protect the shared supply to the PLC's floor.

- A power dip under 10 ms is ridden through. Anything longer stops the PLC, drops all outputs, then auto-restarts — with latched relays and registers retaining their values. See requirement R7.

- The PLC's EFT rating on digital I/O is 1 kV, which is below what a long field cable can present. The reader side is clamped by its own TVS devices; the PLC side is not. Surge protection on the shared supply is the installer's responsibility.

## 3.4 Earthing — the 24 V 0 V rail must be left FLOATING

Do not earth the negative rail of the shared 24 V supply. The reader board's ground is already earthed on site, through the antenna feeder screen and the enclosure earth stud. Earthing the 24 V negative rail is common panel practice — but if both are done, FIELD_COM meets board ground through the earth path and the 2500 Vrms optocoupler barrier becomes decorative. Nothing is damaged. Both nodes sit near 0 V. But it re-creates precisely the ground loop the optocouplers were fitted to break, over a long field cable that may run near traction cable — which is the worst possible place to have one. The PLC chassis stays earthed while its 24 V rail floats. That is the intended arrangement, not a contradiction: Delta requires the chassis be grounded, and the supply-to-chassis insulation is > 5 MΩ at 500 VDC.

One consequence of a floating supply, so nobody is surprised by it later: a first earth fault anywhere on the 24 V system is silent and harmless — it merely references the island. It is the second fault, at a different point, that puts current through earth. If the site wants that first fault to be visible, the tool is an insulation monitor on the 24 V supply, not a bond.

If the site's earthing standard forbids a floating rail, bond it knowingly, record it in the as-built, and accept that the field I/O isolation no longer provides loop-breaking — only surge clamping remains.

# 4. I/O map

Channel names are unique and authoritative. Key your program and your drawings off the channel name (X1, Y0 …), never off the role label.

## 4.1 Reader → PLC  (six signals on X1–X6)

| J26 pin | Reader channel | Signal | PLC input | Meaning |
| --- | --- | --- | --- | --- |
| 1 | OUT1 | SPEED0 | X1 | Conveyor speed code, bit 0 (LSB) |
| 2 | OUT2 | SPEED1 | X2 | Conveyor speed code, bit 1 |
| 3 | OUT3 | SPEED2 | X3 | Conveyor speed code, bit 2 (MSB) |
| 4 | OUT4 | DIRECTION | X4 | Direction of travel |
| 5 | OUT5 | RESULT | X5 | Read verdict — pass and fail on one channel, encoded by pulse width (§5.3) |
| 6 | OUT6 | HEARTBEAT | X6 | Toggles while the reader is alive; goes and stays low when it is safe to cut power (§6) |
| 7 | OUT7 | (parked) | — | Wired to a spare terminal, not to the PLC. No point is free for it (§2.2). |

X0 is deliberately left free. X0–X2 are the 100 kHz high-speed counter inputs and X3–X7 are 10 kHz. The reader's signals are millisecond-class and would waste a fast input. X0 — the fastest — is reserved for a future encoder or wheel sensor. It is the only free point on this PLC. Please do not consume it.

Output polarity, for all six: signal asserted ⇒ the reader's optocoupler pulls the X input to 0 V ⇒ the PLC reads the input ON. Asserted equals ON. There is no inversion anywhere in the chain.

## 4.2 PLC → reader  (three signals on Y0–Y2)

| PLC output | J26 pin | Reader channel | Signal | Meaning |
| --- | --- | --- | --- | --- |
| Y0 | 9 | IN1 | ZONE_ARRIVE | A carton has arrived in the RFID reading zone |
| Y1 | 10 | IN2 | ZONE_EXIT | The carton has left the reading zone |
| Y2 | 11 | IN3 | SHUTDOWN_REQUEST | Five pulses request a controlled shutdown (§6.2) |
| — | 12 | IN4 | (parked) | Wired to a spare terminal, not to the PLC |

Input polarity: Y energised ⇒ +24 V applied to the reader input ⇒ signal asserted. Energised equals asserted.

## 4.3 Panel-local I/O — not part of the field harness

| PLC point | Type | Signal | Meaning |
| --- | --- | --- | --- |
| X7 | Input | SHUTDOWN_BUTTON | Operator push button requesting a controlled shutdown (§6) |
| Y3 | Output | STATUS_LAMP | Single lamp carrying reader state by flash pattern (§6.5) |

A guarded or key-operated push button is recommended. Shutdown is a one-way trip: once the reader has accepted the request, only a power cycle restarts it (R10).

# 5. Signal semantics

## 5.1 SPEED0..2 — a 3-bit binary code

X1, X2 and X3 together carry a binary value from 0 to 7. SPEED0 (X1) is the least significant bit.

| X3 (SPEED2) | X2 (SPEED1) | X1 (SPEED0) | Value | Meaning |
| --- | --- | --- | --- | --- |
| OFF | OFF | OFF | 0 | STOP |
| OFF | OFF | ON | 1 | Speed level 1 (slowest) |
| OFF | ON | OFF | 2 | Speed level 2 |
| OFF | ON | ON | 3 | Speed level 3 |
| ON | OFF | OFF | 4 | Speed level 4 |
| ON | OFF | ON | 5 | Speed level 5 |
| ON | ON | OFF | 6 | Speed level 6 |
| ON | ON | ON | 7 | Speed level 7 (fastest) |

Loss of signal commands STOP — and this must be preserved Every way this system can fail de-asserts the bits, so every failure reads as 000 = stop: • field cable broken or unplugged → 000 → stop • reader unpowered → 000 → stop • reader software crashed or halted → 000 → stop • before the reader's software has even started → 000 → stop The boot case is deliberate, not luck: the outputs are held de-asserted by hardware at power-on, before any software has started. The conveyor is commanded stopped from the instant the reader is powered.

## 5.2 The speed code is not atomic — R1 exists because of this

The three bits do not change together. Optocoupler turn-on and turn-off times differ, so on a multi-bit transition the PLC can briefly latch an intermediate value. A change from 3 to 4 — 011 to 100 — can be read as 111, full speed, if the falling bits lag the rising one.

The DVP's 10 ms input filter absorbs the skew itself, but the three channels' filters expire independently, so a scan boundary can still fall between them. This cannot be fixed on the reader side; nothing in copper can fix it. It is handled in the ladder — see requirement R1.

## 5.3 RESULT (X5) — the read verdict, encoded on one channel

Pass and fail share a single channel. The verdict is carried by the WIDTH of a single pulse, not by which of two wires is asserted and not by a count of pulses.

| Verdict | Pulse on X5 | PLC decodes as |
| --- | --- | --- |
| FAIL | one pulse, 100 ms | measured width 60–200 ms |
| PASS | one pulse, 500 ms | measured width 400–600 ms |
| anything else | any other width, more than one pulse, or no pulse before the deadline | FAIL |

Why width, and not a count of pulses The obvious encoding — one pulse for fail, two for pass — fails in the dangerous direction. All eleven channels share one return, and the design already anticipates cross-channel disturbance arriving on it. A single induced spike adds a pulse, which would upgrade a FAIL to a PASS and put a bad carton into stock silently. With width encoding every plausible corruption lands on FAIL, which is the safe direction: • a spike creates a short pulse → FAIL • a truncated PASS pulse reads short → FAIL • two pulses arrive → FAIL • nothing arrives → FAIL PASS is deliberately the pattern that is hardest to produce by accident: a sustained 500 ms assertion. Noise does not do that.

⚠️ The decoding rule is the requirement, not the timings Decode strictly: measure the width, and treat ONLY a clean single pulse inside the PASS band as PASS. Never infer PASS from “not FAIL”, and never treat an out-of-band pulse as “probably PASS”. A loose decoder is worse than no verdict channel at all, because it converts an obviously-broken signal into a confidently wrong answer.

There is exactly one verdict per carton. There is no “no verdict” outcome: if the reader reaches its deadline without deciding, that is a FAIL and it is sent as a FAIL. The verdict is cleared at the start of the next carton cycle.

Cost of the merge, stated honestly: a PASS now takes up to 500 ms to deliver, where two separate wires asserted immediately. That is time taken out of the carton's transit budget, and it needs checking against the verdict deadline — see Q6 in §11.

## 5.4 DIRECTION (X4)

X4 carries the direction of travel. Which state means which direction is not yet specified — see Q1 in §11. Please do not infer it from the label.

## 5.5 ZONE_ARRIVE and ZONE_EXIT

Y0 tells the reader a carton has arrived in the reading zone; Y1 tells it the carton has left. These are how the PLC frames a read: the reader uses the arrival to know when to start looking and the exit to know the carton is gone.

Whether the reader expects these as edges or as levels held for the duration of occupancy is listed as Q3 in §11 and will be confirmed.

## 5.6 HEARTBEAT (X6) — the reader's proof of life, and its shutdown handshake

Why this channel exists, and why it was worth merging the verdict to get it Because 000 means stop, and because every failure produces 000, a dead reader, a broken cable and a commanded stop are otherwise indistinguishable to the PLC. All three present as SPEED = 000 with every other output off. Worse, a hung reader is not even that: a wedged application holds its outputs at their last value forever, and the line keeps running at whatever speed was last commanded. The heartbeat separates “healthy” from “gone” and from “wedged”. It also carries the shutdown handshake in §6 — heartbeat low means safe to cut power. That is what this channel bought, and it is why RESULT was merged rather than the heartbeat being dropped.

# 6. Clean shutdown and power-up

Why this sequence exists — please read this before implementing it The reader keeps persistent state on non-volatile storage, and it writes to that storage during normal operation. Removing the 24 V while a write is in flight can corrupt it. One item matters more than the rest: the serial-number high-water mark. That record is the only thing preventing the same serial number being written onto two different tags. A duplicate serial silently corrupts the customer's stock data. It is not detectable from the reader afterwards and it is not detectable from the tags — they encode and read back as perfectly valid. It surfaces weeks later as two cartons that claim to be the same carton. That is why the shutdown is a handshake and not a timer. The reader tells you when it has finished; the PLC waits to be told.

## 6.1 The sequence, end to end

| Step | Who | What happens |
| --- | --- | --- |
| 1 | Operator | Presses the shutdown push button (X7) |
| 2 | PLC | Latches “shutdown in progress”, suppresses the heartbeat watchdog (R12), sets the status lamp to SLOW FLASH, and emits five pulses on Y2 → reader IN3 |
| 3 | Reader | Recognises the five-pulse pattern and begins a controlled shutdown |
| 4 | Reader | Stops inventory and drops the RF carrier |
| 5 | Reader | Sets SPEED = 000 and DIRECTION = 0 — the conveyor is commanded stopped |
| 6 | Reader | Finishes or abandons any in-flight tag write, then commits and closes the serial counter |
| 7 | Reader | Flushes every outstanding write and puts its storage into a state that is safe to interrupt |
| 8 | Reader | Drives HEARTBEAT (X6) LOW and leaves it low — this is the “safe to cut power” signal |
| 9 | Reader | Powers itself down |
| 10 | PLC | Sees the heartbeat continuously absent for 3 s, sets the status lamp to FAST FLASH (R11) |
| 11 | Operator | Removes the 24 V supply |

The heartbeat stops at step 8, not step 3. This is the single most important detail in this section. The heartbeat must keep running through the whole shutdown and stop only once the reader's storage is safe. If the heartbeat stopped when the request was received, the PLC would signal “safe” while the reader was still writing — and cutting power there causes exactly the corruption this whole sequence exists to prevent. So: a heartbeat that is still toggling after the button is pressed is the sequence working correctly. It is not a fault and it must not be treated as one.

## 6.2 The five-pulse request — why pulses and not a level

A single steady level on a long field wire can be produced by a wiring fault, a stuck relay contact or induced noise. Five timed transitions cannot. The pattern is a deliberate, recognisable request rather than a state that could be arrived at by accident — the same reasoning that puts the read verdict on a width-encoded pulse in §5.3.

| Parameter | Proposed value | Note |
| --- | --- | --- |
| Pulse count | 5 | Exactly five. Four or six is not a request and is discarded. |
| Pulse ON time | 200 ms | Comfortably above the reader's ≥ 10 ms debounce and the relay's ~10 ms response |
| Pulse OFF time | 200 ms |  |
| Total burst length | ≈ 2 s |  |
| Acceptance window | All five within 5 s | A partial or slow burst is discarded and nothing happens — no shutdown, no error |

These figures are a proposal from our side and are listed as Q4 in §11. The reader firmware must be built to match whatever is agreed, so please build the rung but do not commit to these numbers until they are confirmed.

## 6.3 What the PLC must do if the reader does not respond

Do not declare “safe to power down” on a timeout. If the heartbeat has not stopped within 60 seconds of the request, the reader has not accepted it, or it has failed part-way through. Cutting power at that moment is precisely the hazard this sequence exists to avoid. Raise a fault — status lamp DOUBLE FLASH — and do not show the safe-to-power-down pattern. A human decision to pull power anyway is a legitimate last resort; an automatic one is not. Call us before pulling power on a faulted shutdown if the line can afford to wait. The reader's own logs will say how far it got.

## 6.4 Power-up

On restoration of the 24 V supply the reader boots from cold. Power-on to the application being ready is realistically 20–40 seconds.

| Step | What happens |
| --- | --- |
| 1 | 24 V restored. Status lamp OFF. The heartbeat watchdog stays suppressed (R12). |
| 2 | The reader boots. SPEED reads 000 throughout, because the outputs are off before any software runs. |
| 3 | The heartbeat begins toggling on X6. |
| 4 | The PLC counts at least three clean transitions, then sets the status lamp STEADY and enables the heartbeat watchdog. |

Two things to get right here Do not alarm before 60 seconds. A boot that takes 40 s is normal. A PLC that decides the reader is dead after 10 s will fail every single power-up, and an alarm that fires on normal operation is an alarm that gets ignored. Require three transitions, not one edge. A single edge can be produced by contact bounce or a noise pulse on the shared return. Three consecutive transitions at the expected period cannot.

Note what READY does and does not mean: the heartbeat proves the reader's application is running. Whether it also implies the RFID module is connected and configured is listed as Q5 in §11 — do not assume it does.

## 6.5 The status lamp (Y3) — one lamp, five patterns

Reader-ready and safe-to-power-down were originally two lamps. They are one lamp carrying five states by flash pattern, which is what freed the output to have a lamp at all (§2.2). The patterns are chosen so that the two that matter most are unmistakable from across an aisle: steady means run, fast flash means you may cut power.

| Pattern | Meaning | When |
| --- | --- | --- |
| OFF | No power, or the reader is not yet ready | From 24 V on until three heartbeat transitions are counted (R13) |
| STEADY | Reader ready and running | Heartbeat healthy, no shutdown in progress |
| SLOW FLASH | Shutdown in progress — do NOT cut power | From the button press until the heartbeat has been absent 3 s |
| FAST FLASH | Safe to power down | Heartbeat continuously absent for 3 s after a commanded shutdown (R11) |
| DOUBLE FLASH | Fault | Heartbeat lost outside a shutdown, or a shutdown that did not complete in 60 s |

Suggested rates — adjust to what reads well on the chosen lamp SLOW FLASH ≈ 1 Hz (500 ms on, 500 ms off). FAST FLASH ≈ 4 Hz (125 ms on, 125 ms off). DOUBLE FLASH = two 100 ms pulses then a 1 s pause. These are ergonomics, not interface timing — nothing on the reader side depends on them. Change them if the lamp or the ambient light makes a different choice clearer.

If the site would rather have two lamps It can, but not on this PLC — every point is allocated (§2.2). Two lamps means a 28-point unit or an expansion module, and that is a decision to take before the panel is built rather than after. A second lamp driven from a spare contact of an interposing relay is not an alternative: nothing here has a spare contact, and adding an interposer to gain one is more panel work than the extra I/O.

# 7. Ladder requirements

Fourteen requirements. Each is numbered so it can be signed off individually at commissioning, and each says why it exists — please read the reason as well as the rule, because several of them look optional and are not.

| # | Requirement | Why |
| --- | --- | --- |
| R1 | Require the 3-bit SPEED code to be stable for 2–3 consecutive scans before acting on it. | The code is not atomic (§5.2). Without this, a transition can be read as a spurious intermediate value — including 111, full speed. One scan of a wrong speed against a VFD ramp is minor, but it is a real process fault and the fix is free. |
| R2 | Treat SPEED = 000 as an unconditional command to stop the conveyor. | This is the fail-safe state and every failure mode produces it. It must never be interpreted as “no change” or “hold last speed”. |
| R3 | Leave the input filter D1020 at its 10 ms default. Do not set it to 0. | It is the PLC-side half of the ≥ 10 ms debounce this interface requires. All eleven channels share one return, and that shared return is how cross-channel disturbance arrives. Note the filter is what makes the R9 width measurement trustworthy as well. |
| R4 | Do not consume X0. | Reserved for a future encoder or wheel sensor — it is the only free point on this PLC and the fastest one (§4.1). |
| R5 | Drive Y0–Y2 as clean, debounced signals. Do not chatter them. | The relay outputs respond in ~10 ms and the reader debounces ≥ 10 ms on its side. Rapid toggling wastes relay life for no benefit. Y3 is exempt — the lamp is meant to flash. |
| R6 | Never wire SPEED, DIRECTION, RESULT or HEARTBEAT to anything other than a DVP input. | Not a drive, not a contactor, not a lamp, not a counter module. See §1. The reader's outputs cannot guarantee the current those loads draw, and the failure is intermittent and heat-dependent rather than clean. |
| R7 | Handle resuming mid-state after a power interruption. | A dip over 10 ms stops the PLC and drops all outputs, then auto-restarts with latched relays and registers retaining their values. The program must not assume it starts from a known idle state — in particular it may restart with “shutdown in progress” still latched. |
| R8 | Implement a watchdog on HEARTBEAT (X6). If it stops toggling outside a shutdown or a boot, stop the line and raise a fault. | This is what distinguishes a dead or wedged reader from a commanded stop (§5.6). A wedged reader holds its outputs at their last value and the line runs on at the last commanded speed — the heartbeat is the only thing that catches that. |
| R9 | Decode the RESULT pulse on X5 by measuring its width, strictly. Only a single clean pulse inside the PASS band is a PASS. Everything else is a FAIL. | Pass and fail share one channel (§5.3). A loose decoder converts a corrupted signal into a confident PASS and puts a bad carton into stock silently. Never infer PASS from “not FAIL”, and never accept an out-of-band pulse as “probably PASS”. |
| R10 | On the shutdown button: debounce it, latch the request, emit exactly five pulses on Y2, and do not provide a cancel. | Shutdown is a one-way trip — once the reader has accepted it, only a power cycle restarts it (§6). A cancel button would imply a recovery path that does not exist. Require a deliberate press. |
| R11 | Show FAST FLASH (safe to power down) only when the heartbeat has been continuously absent for 3 seconds following a commanded shutdown. If it has not stopped within 60 seconds of the request, raise a fault and show DOUBLE FLASH instead. | That pattern is a licence to cut power. Showing it on a timeout, or on a momentary gap in the heartbeat, invites exactly the corruption §6 exists to prevent. |
| R12 | Suppress the R8 watchdog during a commanded shutdown and during power-up, until READY is declared. | Otherwise every shutdown raises a “reader dead” fault, and so does every boot. An alarm that fires during normal operation is one that gets ignored — including on the day it is real. |
| R13 | On power-up, require at least three clean heartbeat transitions before declaring READY. Allow at least 60 seconds before treating a missing heartbeat as a fault. | A single edge can be contact bounce. And a cold start to application-ready is realistically 20–40 s — a shorter timeout fails every power-up (§6.4). |
| R14 | Drive the status lamp (Y3) to the five patterns of §6.5, and to no others. | One lamp carries reader-ready, shutdown-in-progress, safe-to-power-down and fault. An extra improvised pattern makes the four that matter ambiguous. If a new state needs showing, tell us and we will agree a pattern. |

R8, R9, R10, R11 and R13 all depend on firmware we have not yet released The channels are wired and specified here, but four reader-side behaviours are still in progress on our side: toggling the heartbeat, recognising the five-pulse request, driving the heartbeat low at the end of shutdown, and encoding the verdict as a width-coded pulse. Please build the rungs. We will confirm the pulse timings (Q2, Q4), the heartbeat period (Q5) and the verdict deadline (Q6), and we will tell you when the firmware is available. Until then X5 and X6 sit static. Do not let a static X6 hold the conveyor stopped or raise a permanent fault in the interim — make R8 alarm-only, or disable it, until we confirm.

# 8. Safety statement — please read before design

This interface is NOT a safety function. SPEED = 000 is a CONTROL stop, not a safety stop. The speed command is an encoded value carried on three non-atomic channels. That makes it a control signal; it could not be a safety function whatever the intent. The Intelli-RFID Reader is not in the safety chain. The conveyor's safety stop must be provided by its own rated architecture — E-stop, safety relay, or whatever the machine builder has fitted — and must NOT pass through J26, the PLC's X inputs, or any part of the reader. The shutdown push button of §6 is a controlled-shutdown request, not an emergency stop, and must not be labelled, coloured or positioned as one. It must not be a mushroom head, and it must not be red on yellow. No performance level (PL) or safety integrity level (SIL) claim attaches to this interface, and none may be made for it in any document, quotation or manual. The fail-safe behaviour described in §5.1 is a real and useful property. It is not a safety rating, and the two must never be conflated.

What we need you to confirm — the negative That nothing in the conveyor's safety function depends on our SPEED = 000. Cheap to ask, expensive to assume. If any part of the existing safety design currently relies on the reader commanding stop, it needs to be re-architected before commissioning, not discovered during it.

“Control stop” does not mean unimportant. Failing to stop on command still means pile-up, jams and product damage, and R9 getting a verdict wrong still means bad stock data. It sets the class of these requirements, not their priority. R1, R2 and R9 all remain requirements — they are availability and correctness requirements rather than safety ones.

# 9. Enclosure and environment

The PLC cannot go where the reader goes. The DVP-SA2 is rated 0–55 °C, non-condensing, and is an OPEN TYPE device requiring a control cabinet. The Intelli-RFID Reader is designed to a −40 … +85 °C target for an unconditioned field enclosure. In an Indian unconditioned enclosure a 0–55 °C non-condensing part is outside its rating on a summer afternoon, and again on a monsoon morning.

|  | Intelli-RFID Reader | Delta DVP-SA2 |
| --- | --- | --- |
| Operating temperature | −40 … +85 °C (design target) | 0 … 55 °C |
| Storage temperature | — | −25 … 70 °C |
| Condensation | — | Non-condensing only |
| Enclosure | Designed for an unconditioned field enclosure | OPEN TYPE — control cabinet mandatory |

Two workable arrangements:

- PLC in a controlled panel, reader at the tunnel, with the 12-core field harness between them. This is preferred. It also puts the shared 24 V supply, the push button and the status lamp in the panel, where the operator is.

- Both in one enclosure — then the enclosure must hold 0–55 °C non-condensing, which means heating, ventilation or both. That becomes a system requirement and needs to be priced, not assumed.

This cannot be fixed in either device's design. It belongs in the installation documentation before a quotation is written against it.

# 10. Commissioning checklist

Work through these in order. Items 1–4 are wiring and must pass before the reader is powered against the PLC.

| # | Check | Pass criterion |
| --- | --- | --- |
| 1 | S/S is strapped to +24 V and has not been reversed | With S/S at +24 V and a reader output asserted, the corresponding X indicator lights. If no output ever turns on, suspect S/S first. |
| 2 | C0 is fed from +24 V, not from 0 V | Energising Y0 applies +24 V to J26 pin 9 with respect to pin 8. All four outputs share C0 on this model. |
| 3 | FIELD_COM (J26 pin 8) is connected to the supply 0 V | Continuity from J26 pin 8 to the PLC 0V terminal. Without this nothing works in either direction. |
| 4 | The shared 24 V 0 V rail is FLOATING | No continuity from the 24 V negative to panel earth. Verify at commissioning — an as-built can drift from an intention. |
| 5 | D1020 is at its 10 ms default | Read the value; it must not be 0 |
| 6 | OUT7 and IN4 are parked, labelled and NOT on PLC points | Two spare terminals, marked on the drawing (§3.1) |
| 7 | One channel end to end, reader → PLC | Assert OUT1 and confirm the X1 indicator lights |
| 8 | One channel end to end, PLC → reader | Energise Y0 and confirm the reader reports the input asserted |
| 9 | Measure V_CE across a closed reader output | OUT1 to FIELD_COM, PLC wired and powered. Record the value and send it to us — see the note below. |
| 10 | SPEED code stability rule (R1) behaves | Force a 3→4 transition and confirm the ladder does not act on an intermediate value |
| 11 | Loss-of-signal produces STOP | Unplug the field connector and confirm the conveyor is commanded stopped |
| 12 | Verdict decode (R9) — PASS | Inject a 500 ms pulse on X5 and confirm the ladder registers PASS |
| 13 | Verdict decode (R9) — FAIL | Inject a 100 ms pulse and confirm FAIL |
| 14 | Verdict decode (R9) — the important one | Inject a 300 ms pulse, and separately two 100 ms pulses 100 ms apart. Both must decode as FAIL. If either produces a PASS, the decoder is wrong and must be fixed before the line runs. |
| 15 | Heartbeat watchdog (R8) fires | With the reader running normally, unplug the field connector and confirm the line stops and the lamp shows DOUBLE FLASH |
| 16 | Full shutdown sequence (R10, R11, R14) | Press the button; confirm five pulses on Y2, the lamp going SLOW FLASH, the heartbeat continuing for several seconds, then stopping, then the lamp going FAST FLASH. Confirm no fault is raised during it (R12). |
| 17 | Shutdown timeout behaves | Simulate a reader that does not respond (leave Y2 disconnected). Confirm a fault at 60 s and that FAST FLASH is never shown. |
| 18 | Power-up sequence (R13) | Restore 24 V. Confirm no fault during boot, and the lamp going STEADY only after the heartbeat is established. |
| 19 | The reader really did shut down cleanly | After a full cycle, confirm with us that the reader's logs show a clean shutdown and the serial counter is intact. This is the point of the whole sequence. |

Item 9 — one measurement that settles an open engineering question The reader's outputs drive the PLC's inputs directly, with no booster in the path. Our margin analysis says that is sound, but it rests partly on a traced datasheet curve rather than a guaranteed figure. A single reading retires the question. Measure the voltage across a closed output (OUT1 to FIELD_COM) with the PLC wired and powered: • near 0.5 V → the output is in deep saturation, far from its limit, and there is ample margin for the life of the installation • near 5 V → the design is sitting at its guarantee anchor and we will want to review the installation temperature Please record it and send it back with the commissioning report. It takes one minute and it is worth more than the whole analysis.

Item 14 is the one to insist on Items 12 and 13 confirm the decoder recognises the two valid patterns. Only item 14 confirms it rejects everything else — and rejecting everything else is the entire safety of the merged channel. A decoder that passes 12 and 13 but fails 14 will work perfectly on the bench and will, eventually, mark a failed carton as read.

# 11. What we still need to confirm

Six of these are needed before the ladder can be finished. They are listed with who owns them.

| # | Question | Owner | Blocks |
| --- | --- | --- | --- |
| Q1 | DIRECTION polarity — which state means which direction? | IntelliRail | Yes — §5.4 |
| Q2 | RESULT pulse widths — confirm or replace the 100 ms FAIL / 500 ms PASS and the 60–200 / 400–600 ms decode bands proposed in §5.3 | IntelliRail | Yes — R9 |
| Q3 | ZONE_ARRIVE / ZONE_EXIT — edge-triggered or level-held for occupancy? | IntelliRail | Yes — §5.5 |
| Q4 | Five-pulse timing — confirm or replace the 200 ms / 200 ms / 5 s window proposed in §6.2 | IntelliRail | Yes — R10 |
| Q5 | Heartbeat period and watchdog tolerance — and whether “heartbeat present” also means the RFID module is connected and configured, or only that the application is running | IntelliRail | Yes — R8, R13 |
| Q6 | Verdict latency — a PASS now takes up to 500 ms to deliver (§5.3). Does that fit inside the carton's transit time between the reading zone and the divert or reject point? | Both | Yes — §5.3 |
| Q7 | Confirm nothing in the conveyor's safety function depends on SPEED = 000 | Integrator | No — but must be answered before commissioning (§8) |
| Q8 | Confirm the enclosure arrangement of §9 and get it into the installation specification | Both | No |
| Q9 | Speed levels 1–7 — what physical conveyor speed does each correspond to? | Both | No — needed for VFD parameterisation |

Q6 is the one we would like an answer to first It is the only question here that could change the electrical design rather than just a number in the ladder. If 500 ms does not fit the transit budget, the honest answer is not to shorten the PASS pulse — that erodes the margin that makes the encoding safe. It is to go to a 28-point unit and put PASS and FAIL back on separate wires. So please measure or calculate the available window before the panel is built. Tell us the number even if it is comfortable.

Please do not infer Q1–Q6 from the signal names. They are genuinely unspecified rather than merely undocumented. Guessing them will produce a ladder that appears to work on the bench and misbehaves on the first real carton.

# Appendix A. Quick reference

## A.1 Terminal summary

| PLC terminal | Connects to | Note |
| --- | --- | --- |
| 24V | Field supply +24 V |  |
| 0V | Field supply 0 V | Same rail as J26 pin 8. Leave the rail floating — §3.4 |
| S/S | Field supply +24 V | Jumper to C0. Reversing this kills all six reader outputs silently. |
| C0 | Field supply +24 V | Relay common for all four Y outputs. This is the +24 V side, NOT a ground. |
| X0 | — (not used) | Reserved, 100 kHz counter input — leave free (R4) |
| X1 … X6 | J26 pins 1 … 6 | Reader outputs. Asserted = input ON |
| X7 | Shutdown push button | Panel-local |
| Y0 … Y2 | J26 pins 9 … 11 | Reader inputs. Energised = asserted |
| Y3 | Status lamp | Panel-local. Lamp between Y3 and 0 V |
| (spare terminals) | J26 pin 7 (OUT7), J26 pin 12 (IN4) | Parked. Wired to the reader, not to the PLC — no point is free (§2.2) |

## A.2 One-line summary of each signal

| Signal | Point | One line |
| --- | --- | --- |
| SPEED0..2 | X1–X3 | 3-bit binary conveyor speed, 0–7. 000 = stop. Requires the R1 stability rule. |
| DIRECTION | X4 | Direction of travel. Polarity to be confirmed — Q1. |
| RESULT | X5 | Read verdict on one channel: 100 ms pulse = FAIL, 500 ms pulse = PASS, anything else = FAIL. Decode strictly — R9. |
| HEARTBEAT | X6 | Toggles while alive. Low and staying low after a commanded shutdown = safe to cut power. R8, R11, R13. |
| SHUTDOWN_BUTTON | X7 | Operator request. Debounced, latched, no cancel — R10. |
| ZONE_ARRIVE | Y0 | Carton has arrived in the reading zone. Edge or level to be confirmed — Q3. |
| ZONE_EXIT | Y1 | Carton has left the reading zone. Edge or level to be confirmed — Q3. |
| SHUTDOWN_REQUEST | Y2 | Five pulses request a controlled shutdown — §6.2. |
| STATUS_LAMP | Y3 | Five patterns: OFF, STEADY, SLOW, FAST, DOUBLE — §6.5, R14. |

## A.3 The two encoded signals, in one line each

The read verdict one 500 ms pulse on X5 = PASS. Everything else, including one 100 ms pulse, any other width, more than one pulse, or silence = FAIL. PASS is the pattern that is hardest to produce by accident. That is the whole design — §5.3.

The shutdown handshake Button → 5 pulses on Y2 → reader commits its state → heartbeat stops → FAST FLASH → cut 24 V The heartbeat stops at the END of the reader's work, not at the start. That ordering is the whole point — §6.1.

End of document — IntelliRail, revision 1.0, 30 August 2026